Residential Humidifier Specification

(ITALICIZED ITEMS REQUIRE SELECTION AND EDITING)

Supply (a) Neptronic immersion humidifier(s) series SKR, as manufactured by N.E.P. complete with:

- On/Off operation

- Incoloy 800/825 electric elements

- Permanent, cleanable stainless steel evaporation chamber

- Unidirectional, plug- in connectors with flexible wiring (BX (Greenfield) not acceptable)

- Single fill/drain connection

- Siphon system with no solenoid drain valve

- Internal controls to temper drain water to below 140F at the outlet of the humidifier

- Water level control system

- Microprocessor control

- High temperature safety element

- SAM steam distribution manifold ((7/8” diameter, 9” long for SKR14 & SKR25) or (1 3/8” diameter, 14” long for SKR30 & SKR40))

- Airflow proving switch

- Control connections shall be made using 2 furnished, pre-assembled cables with telephone jacks (50’for room humidistat and 10’ for flow switch and/or optional high limit duct humidistat)

- 6’ flexible steam hose

- Dry contact (3Amp/24Vac) to start the supply fan on call for humidity

- Remote alarm dry contact (1A/24Vac)

- CSA approval

- (Room humidity controller with setpoint adjustment) or (Duct humidity controller with setpoint adjustment) or (Duct humidity controller with room setpoint controller including one (1) extra 10’ cable with telephone jacks)

- Capacity: (4.5 or 7.5 or 9 or 12) lbs/hr

- Power supply: (120V/1Ph/60 Hz 4.5 lbs/hr only) or (240V/1Ph/60Hz or 208V/1Ph/60Hz for all other models)

- Model: Neptronic SKR (14 Casa or 25 Villa or 30 Chateau or 40 Belvedere)

OPTIONS:

- Integrated airflow switch and high limit duct humidistat (Replaces airflow switch above)

- OTW temperature sensor to be installed on a window pane and wired to the Neptronic room or duct humidity controller to prevent fogging on windows

THE FOLLOWING OPTION IS TO BE USED WITH A BMS SYSTEM OR STANDARD ELECTROMECHANICAL CONTROLS ONLY.  NO CABLES WITH TELEPHONE JACKS, NO ELECTRONIC AIR FLOW SWITCH AND NO HUMIDITY CONTROLLERS ARE INCLUDED. THE OTW AND INTEGRATED AIRFLOW SWITCH AND HIGH LIMIT DUCT HUMIDISTAT OPTIONS ABOVE ARE NOT AVAILABLE. SPECIFY IF A HUMIDISTAT, A MECHANICAL AIR FLOW SWITCH AND HIGH LIMIT ARE TO BE FURNISHED BY NEPTRONIC OR BY OTHERS. REMOVE ITEMS ABOVE REFERRING TO PRE-ASSEMBLED CABLES WITH TELEPHONE JACKS.

- Two (2) terminal blocks to wire the humidistat and the safeties.