Residential Humidifier Specification (SDU)

(ITALICIZED ITEMS REQUIRE SELECTION AND EDITING)

Supply (a) Neptronic immersion humidifier(s) series SKR, as manufactured by N.E.P. complete with:

- Modulating operation.  To modulate 0-100% of the capacity. Modulation of element shall be achieved with hybrid SSR's using zero voltage crossing.  The hybrid SSR's will be backed up by an electro-mechanical contactor.  To avoid harmonics and peak electrical loads, Time Proportioning modulation using only electro-mechanical relays will not be acceptable.

Or

- On/Off operation

- Incoloy 800/825 electric elements

- Permanent, cleanable stainless steel evaporation chamber

- Unidirectional, plug- in connectors with flexible wiring (BX (Greenfield) not acceptable)

- Single fill/drain connection

- Siphon system with no solenoid drain valve

- Internal controls to temper drain water to below 60C at the outlet of the humidifier

- Water level control system

- Microprocessor control

- High temperature safety element

- SDU space distribution unit (mounted on the SKR unit)

- Airflow proving switch (integrated to the SDU)

- Dry contact (3Amp/24Vac) to start the supply fan on call for humidity

- Remote alarm dry contact (1A/24Vac)

- CE and CSA approval

- Capacity: (3, 3.75 or 5) kg/hr

- Power supply: (230vac/1Ph50 Hz)

- Model: Neptronic SKR (3E Villa or 4E Chateau or 5E Belvedere)

OPTIONS:

- The unit shall be supplied with the appropriate proportional programmable controller HRO20 (Room) with digital display.

Or

- Control connection shall be made using 1 furnished, pre-assembled cable with telephone jacks (15m for room humidity controller with setpoint adjustment).